# HISTORY

First heat pump aplications are considered in the 1920 s with restatements of and improvements on Thomson paper by Krauss and Morley and although there where no heat pumps as such in existence it was possible to examine their feasibility from analysis of the per formance of the rapitly increasing amount of refrigeration equipment which was being installed. This was done by Haldane, who analysed data from a selection of refrigerating plant operation beween 1981 and 1926.

The first major heat pump installation in Europe was commisioned during the period 1938 – 39 in Zurich. This unit, which used river water as the heat source, utilised a rotary compressor with R12 as the working fluid. Used to heat the Town Hall, the output of the Zurıch heat pump was 175 KW, delivering water at a temperature of 600 for space heating. A thermal storage system was incorporated in the circuit, in the form of a calorifier which could be boosted by electric heating at periods of peak demand.

The first heat pump installed in the United Kingdom which succesfully demostrated that a large building could be heated using this technique was located in the Norwich. The unit was installed in the offices of the Norvich Corporation Electricity Department. The heat source used was a river and the heat sink was circulating hot water, delivered at a temperature of 49 0C. Sulphur dioxide (SO2) was used as the refrigerant and ‘coefficient of performance’ of the order of 3 were achieved.

The heat pump installed at Nuffield College, oxfort, (which is still in existance although not operating). Was first conceived in 1954. The system used low grade heat available in sewage as the heat source. The temperature of the sewage was between 16 and 24 0C. The compressor was driven by a 31 KW diesel engine, giving an overall cop of about 4.

In the late 1940 s that the realisation grew that heat pump development and marketing would best be met if ‘unitary’ system were produced. In the full year of production approximately 1000units left the factories in 1952. This had doubled by 1954 and increased tenfold by 1957. In 1963 7600 units were manufactured. The majority of of these units were installed in southern areas of USA, where the need for summer cooling existed, as the necessity for heating in winter, enabling the heat pump to complete effectively with heating – only conventional systems, based on boilers.

Finally, newadays heat pumps are very popular on for cooling and hetaing operations: Hence almost ever commercial building use such systems.

# HEAT PUMP SYSTEMS

Heat pumps are generally more expensive to purchase and install than other hetaing systems but they save money in the long run in some areas because they lower the heating bill. Despite their relatively higher initial cost, the popularity of heat pumps is increasing. About one – third of all single – family homesbuilt in the United States in 1984 are heated by heat pumps.

The most common energy source for heat pump is is atmospheric air (air – to – air systems), although water and soil are also used. The major problem with air – source system is frosting which occurs in humid climates when the temperature falls below 2 to 5 0C. The frost accumulation on the evaporator coils is highly undesirable since it seriously disrupts the heat transfer. The coils can be defrosted however, by reversing the heat pump cycle (running it as an air conditioner). This result in a reduction in the efficiency of the system. Water source systems usually use well water from depths of up to 80m in the temperature range of 5 to 18 0C, and they do not have a frosting problem. They typically have higher COP’s but are more complex and require easy access to a large body of water such as undergraund water. Soil – Source systems are also rather involved since they require long tubing placed deep in the ground where the soil temperatur is relatively constant. The COP of heat pumps usually ranges between 1.5 and 4, depending on the particular system used and the temperature of the source.

Both the capacity and the efficiency of a heat pump fall significantly at low temperatures. There fare, most air source heat pumps reguire a supplementary heating system such as electric resistance heaters  an oil or gas furnace. Since water and soil temperatures do not fluctuate much, supplementary heating may not be required for water source or soil systems. But the heat pump system must be large enough to meet the maximum heating load.

Heat pumps and air conditioners have the same mechanical components. Therefore it is not economical to have two seperate systems to meet the heating and cooling reguirements of a building or a house. One system can be used as a heat pump in winter and an air conditioner in summer. This is accomplished by adding a reversing valve to the cycle as shown in Figure.

# HEAT PUMPS ACCORDING TO THERMODYNAMICS CYCLE

## Vapour Compression Heat Pumps

The simple Vapour Compression heat pumps are the most widely used systems. The ordinary vapour – compression heat pumps systems are sımple, inexpensive, reliable and practically maintenance – free. Hewever for large industrial applications efficiency not simplicity is the major concern.

The main ports of these systems are compressor, evaporator, condenser and expansion device. There is a refrigerant (working fluid) in the system. It change phase at useful temperatures and pressures. It absorb heat by evaporation and it deliver heat by condensation.

Compressor

Low pressure

high pressure

Expansion Device

Low pressure

high pressure

Condenser

(high

temprature)

Euaporatur

(low

temprature)

Fig:A Basic Vapour Compression Heat Pumps

## Absorption Cycle Heat Pump

Another form of refrigeration which becomes economically attractive when there is a source of inexpensive heat energy at a temperature of 100 to 200 0C is absorption refrigeration.

As the name implies, absorption refrigeration systems involve the absorption of a refrigerant by a transport medium. The most widely used absorption refrigeration system is the ammonia – water system, where ammonia (NH3)serves as the refrigerant and water (H2O) as the transport medium other absorption refrigeration systems include water lithium bromide and water – lithium chloride systems. Where water serves as the refrigerant.

The basic components of an absorption cycle heat pump are the condenser evoporator and main expansion device are all as in vapour compression unit but the compressor is replaced by an absorber a generator and a small pump.

Generator

Condenser

Absorber

Evaporator

Heat suplied

Expension

device

Concentrated

Solution

pump

Heat removed

Figure: Absorption cycle heat pump

## Thermoelectric Heat Pumps

Consider two wires mode from different metals joined at both ends forming a closed circuit. Ordinarily, nothing will happen. But when one of the ends is heated something interesting hoppens: A current flow continously in the circuit. The circuit which incorporates both thermal and electrical effects is called a thermoelectric circuit and a device that operates on this circuit is called a thermoelectric device.

Thermoelectrical devices will not be competitive with vapour compressions heat pumps in the foreseable future, but they may find increasing use in specialised cooling applications where power reguirements are low or where silent operation is necessary close temperature control of electronic components and cold stores in nuclear submarines are examples of these.

## Role Of Domestic Heat Pump

The primary energy uses in a house are for space heating, full air conditioning in climates which necessitate this, and the provision of domestic hot water for washing and other services. A refrigeration duty associated with the storage of perishable foodstuffs is also a common requirement.

A packaged heat pump should be capable of providing the space heating and air conditioning requirements. It is also desirable to use the heat pump to provide at least a part of the domestic hot water requirements. Heat pumps can be linked to refrigeration duties but the domestic refrigeration load of typically  0,5 KW, including a deep freeze, offers little scope for use of the heat rejected at the condenser. In commercial and industrial and premises, however, as will be seen later, the linking of refrigeration and heathing duties can be of considerable economic benefit.

## Heat Sources

Heat pumps may be classified according to their heat source. Ambient source heat pumps abstract heat from a source external to the process or building to which heat is supplied. Heat recovery devices use heat produce as a by product of some other process such as cooling. The more commonly advocated source of heat for both classes of heat pump are considered below.

- Air source heat pumps

- Water source heat pumps

- Ground source heat pumps

- Solor heat sources

- Waste heat as a heat pump heat source

- Geothermal Energy

### Air Source Heat Pumps

Most commercially available domestic heat pump systems use outside air as the heat source and this has been the case since the heat pump was introduced into the domestic scene. Most air source heat pumps woking on the vapour compression cycle also use air as the heat sink.

With single stage vapour compression refrigeration eguipment, air source heat pumps may be operated down to –15 0C to –20 0C, but their effectiveness is low at such temperatures and they are seldom used on their own for heating applications where air temperatures fall below about 2 0C.

While ambient air is the most convenient heat source for obvious reasons, it also suffers from a number of disadvantages which necessitate careful optimisation of their desing, depending upon location. These are largely concerned with the fact that ambient air can vary considerably in its temperature.

### Water Source Heat Pumps

Natural surface water as lakes, seas, and rivers is also a source of heat for heat pumps, and has been used in many installations, both in domestic and commercial buildings. However, difficulties similar to those with air source heat pumps can arise in the winter. Although the water source may be at 6 or 7 0C entering the evoporator heat exchanger, care must be taken not to cool it to 0 0C, because freezing can occur. By increasing the flow rate of the water, the temperature drop throgh the evaporator can be kept as low as 1 – 2 0C. The  use of water as a heat source was tried in an early domestic heat pump constructed by sumner with some success.

The high thermal capacity of water and its good heat transfer characteristics make it and attractive heat source. Water is an excellent heat source where it is readily available in sufficient quantities which do not freeze in winter.

### Ground Source Heat Pumps (Soil)

Despite the low level of geothermal heat, the earth may be used as an effective medium from which to draw heat. Both the movement of ground water and the incident solar radiation heat up the surface layer of soil and heat may be extracted from this layer by means of a heat pump.

The main advantages of soil as a heat source are its relatively steady temperature, the lack of any need to remove frost from heat exchanger surfaces and the elimination of a potentially noisy fan.

### Solor Heat Sources

All heat pump sources are influenced by solar energy to a greater or lesser extent, but solar energy may be hardnessed for heat pump use by solar collectors employing a circulating fluid, by the use of solar energy to raise the temperature of the air approaching the evaporator or by solar cocentrators.

The main advantage of solar energy, whether it be collected via flat plate colectors, concentrators, or, to a less extent, supple menting air sources for heat pumps, is its temperature. By being able to provide heat for the evaporator at a higher temperature than that normally available in conventional air, ground or water sources, the heat pump COP may be raised.

### Waste Heat As A Heat Pump Heat Source

The most common proposals for waste heat recovery in the home associated with heat pumps normally use waste water as a heat source. Heat sources feeding this store include a bath or shower, dishwasher, and washing machine and the heat is upgraded to feed the domestic hot water tank. Other proposals include the recovery of heat from domestic sewage to supplement these sources. Many proposals do of course provide for further heating of the storage medium by solar collectors.

### Geothermal Energy

Tens of thousands of homes are being built or retrofitted with geothermal heating and cooling systems every year, because of the advantages these systems offer ; economical operation noise reduction and product quality initially reversed for the most expensive homes, now these systems heve become affordable options for thausands of low and moderate income housing units because of the systems low life cycle costs compored to all other alternetives in almost every region of the country.

## Heat Storage

The storage of heat and its economic implications for the domestic heat pump are subjects of some considerable debate and no clear answers can be given yet to the question: Should heat storage be used in the home to supply heat to the heat pump evaporator?

As we know the heat sources available for domestic heat pump systems, if they are to be commercially attaractive to manufactures wishing to produce in guantity are susceptible to seassonal and daily temp. Variations which unfortunately lead to lower COP’s at times when the buılding heating demand is greatest (in cold weather with low solar gain and during the night). The expense of direct supplement electric heating, as advocated by many heat pump manufacturers, has led to the search for alternative solutions to this problem, and the storage of heat collected during the summer or on winter days when solar energy can be effectively utilised is a promising technique.

### Sensible Heat Storage

Sensible heat storage media are normally either liguid or solid, and do not undergo a phase change when heat is introduced to or removed from them. Instead they undergo a temperature change.

The most common sensible heat storage medium is water. A part from being readily available, water as a heat storage medium has one unique advantage in that it can be removed from the store for use with out the necessity for a heat exchanger (unless it is used to heat a ducted air system). Water as a heat storage medium can be stored in metallic, concrete or plastic storage vessels.

### Heat Of Fusion Storage Media

The use of the heat of fusion of materials for heat storage, as with sensible heat storage techniques is determined largely by the volume capacity of the material. In the case of latent heat of fusion materials, however, the volume needed is a function of the heat of fusion of the material used.

### Heat Pumps Employing Heat Storage

Many studies have been carried out on the affect that heat storage might have on the performance of a heat pump for domastic heating and air conditioning and of these have also been associated with solar collectors.

## Commercially Available Systems

The number of manufacturers of heat pump systems, particularly in the domestic and commercial and building sectors is very high. The purpose of this section is to present data  on a number of commercially available heat pumps used in houses, with a board geographical spread as for as applications are concerned.

### Air – Air Heat Pump

At this kind of heat pump, heat is carried by air at conderser and evaporator. If heat pump will be used for air – conditioning heating or cooling air is sent directly to the places. These hind of heat pump may be in the form of a single pockage or may be ‘split’.

### Air – Water And Water – Water Systems

A number of  heat pump systems are available for domestic use, based on the use of water as the heat source and / or water sink.

The availability of water as a heat source is not universal, one area in which the Friedrich heat pump does offer innovation is the provision of a hot water generator for providing domestic hot water.

Both air and water can be used as a carrying fluid in this kind of system. If the heat source is air, heat is carried by water at condenser and evaporator. Heating need of houses of factories can be supplied by hot water which exist in the hot water tank.

# HEAT PUMP COMPONENETS

## Compressors

Compressors is the device for increasing the pressure of a gas by mechanically decreasing its volume. Air is the most freguently compressed gas but natural gas, oxygen, nitrogen and other industrially important gases are also compressed. The high operating temperatures and wide range of operating conditions likely to be met in space heating heat pumps make greater demands on compressors than do air – conditioning applications.

### Compressors Types

The four most common types of refrigeration compressors are the reciprocating, screw, centrifugal and vane.

The reciprocating compressor consists of a piston moving back and forth in a cylinder with suction and discharge valves arranged to allow pumping to take place.

Centrifugal compressors increase the kinetic energy of the gas with a high speed impeller and then convert this energy into increased pressure in a divergent outlet passage called the diffuser. Centrifugal compressors are particularly suited for compressing large volumes of gas to moderate pressures. The centrifugal compressor is a well developed machine because of its use in the compression stage of small gas turbines.

Screw compressor consists of two rotors running together within a sealing sleeve. The rotors are identified as ‘male’ and ‘female’. The male rotor has a number of lobes on it which are semicircular in section and formed in a helix along the rotor body. The female rotor has a number of flutes and channels in it, formed in the opposite helix to the male.

Vane compressors operating normally with low compression ratios and low pressures. These compressors are usually found in applications of less than 5 KW drive, generally a great deal less. Discharge pressures seldom exceed 10 bar and pressure differences are limited about 4 bar.

## Condensers

Condensers is a heat exchanger in which steam or vapor losses heat and returns to liquid form. It is used in steam plants and refrigeration systems. In a steam plant, the exhaust steam dischanges into the condenser so that the water and the heat can be recovered from the steam. In a refrigeration system, the condenser removes the heat picked up in the evaporator and the heat of compression, from the refrigerant vapor. The two most common types of condenser are the air – cooled condenser and the shell – and – tube condenser.

An air – cooled condenser is used in automobile air conditioners, refrigerators, and home air conditioners. It has a long tube with many metal fins attached. Hot, high – pressure refrigerant vapour passes through the tube. Heat from the vapour transfers to the tube and then to the attached fins. Cooler air flows between the fins and carries away the heat.

In a shell – and – tube condenser, the tubes are contained within a shell, or container, which usually has cool water flowing through it. As the steam or vapour passes through the tubes and condensers, the cool water circulates around the tubes to carry away the heat.

## Evaporators

In most refrigerating evaporators the refrigerant boils in the tubes and cools the fluid that passes over the outside of the tubes and cools the fluid that passes over the outside of the tubes. Evoporators that boil refrigerant in the tubes are often called direct – expansion evaporators.

Direct – expansion evaperators used for air – conditioning applications are usually fed by an expansion valve that regulates the flow of liguid so that the refrigerant vapour leaves the evaporator with some superheat.

Another concept is the liquid – recirculation or liquid – overfeed evaporator in which excess liqıid at low pressure and temperature is pumped to the evaperator. Some liquid boils in the evaporator and the remainder floods out of the outlet. The liquid from the evaporator is seperated out, and the vapour flows on to the compressor. Low – temperature industrial refrigeration system often use this type of evaporator, which has the advantage of wetting all the interior surfaces of the evaporator and maintaining a high coefficient of heat transfer.

## Expansion Devices

The purpose of the expansion device is two fold: It must reduce the pressure of the liguid refrigerant, and it must regulate the flow of refrigerant to the evaporator.

The control, expansion device must match the flow of refrigerant to the load on the evoporator, the pumping capacity of the compressor, and the ability of the condenser to reject heat. It determines the capacity the system, which is probably the most important functions in the entire system.

Expansion in the devices for controlling the refrigerant flow in heat pumps are normally thermostatic expansion valves.

## Capillary Tubes

The capillary tube serves almost all small refrigeration systems, and its application extends up to refrigerating capacities of the order of 10 KW. A capillary tube is 1 to 6 m. Long with an inside diameter generally from 0,5 to 2 mm. The name is misnomer, since the bore is too large to permit capillary action. Liguid enters the capillary tube and as it flows through the tube, the pressure drops because of friction and acceleration of the refrigerant. Some of the liqıid flashes into vapor as the refrigerant flows through the tube.

## Presostat

It is used to prevent the below or above the desired pressure. If pressure increase this can damage the compressor. But we use presostat that stops the compressor when the pressure increase or decrease.

## Thermostat

It is used to prevent the condenser that may heat extremely or occur the high pressure. In addition the circulation pump and fancoil are conceled if the desired temperature on condenser decrease. After the circulation pump and fan coil are concelled, the desired temperature of condenser are provided.

## Reversing Valves

A reversing valve changes the system from cooling to the heating mode. This change over requires the use of a valve or valves in the refrigerant circuit. Reversing valves are usually pilot operated by means of solenoid valves, which admit head suction pressures to move the operating elements.

## Filter – Drier

Filter  - Drier is used to clean out any dirt and remove water that can clog the expension device. A filter – drier is designed to remove both solids and undesirable soluble, like water and acid, from the refrigerant. There are several types of filter – driers, but most combine an activated alumina desiccant with a molecular sieve. Filter are located in the liqıid line, usually near the condensing unit. Whenever the compressor must be changed because of a burnout, the liguid line drier should also be changed.

## Heat Exchangers

Heat exchangers, any of several devices that transfer heat from a hot to cold fluid. In many engineering applications it is desirable to increase the temperature of one fluid while cooling another. This double actions is economically accomplished by a heat exchanger. Heat exchangers are used extensively in fossil – fuel and nuclear passes plonts, gas turbines, heating and air conditionng, refrigeration, and the chemical industry. The devices are given different names when they serve a special purpose. Thus boilers, evaporators, superheaters, condensers and coolers may all be considered heat exchangers.

Heat exchangers are manufactured with various flow air arrangements and in different designs. Perhaps the simplest is the concentric tube or double – pipe heat exchanger. In which one pipe is placed inside another. These heat exchangers are built in several ways, such as a coil or in straight sections placed side by side and connected in series.

# DOMESTIC HEAT PUMP APPLICATIONS

In any country, the first significant heat pump installation are not in houses, but in large commercial building because it is in commercial or industrial applications that the largest energy saving from single heat pump installations will be mode. Despite this fact, heat pump applications in the home are worthy of detailed consideration for two main reasons. Heat pumps can have the greatest impact on national energy swing in the domestic sector, because there are many more houses than other types of buildings.

## Space Heating

For simple space heathing, the domestic user is accustomed to either a wet central heating system, in which hot water is circuted to radiators located in each room, or to a ducted air system, in which a warm air is blown into each room. Induvidual room heaters such as radiators, storage units and convectors are also widely used, often as a supplementory heat source to back up the central system.

As a device for space heating, the heat pump need not function on the basis of a central system serving a number of rooms. Individual room conditioners may be installed, each with its own compressor and condenser, with either an internal or external heat source for the evaporator.

## Food Storage

Heat from enclosed food storage cabinets has from time to time been suggested as possible energy source for heat pumping to provide space or water heating.

In food storage equipment, reliability is most important factor and factory sealed refrigerator and freezer refrigeration systems have been developed to very high standard of reliability. To ambient such factor units with water heater, using on – site pipe work and interconnections, would reduce this level of reliability.

It seems unlikely that the possible loss of reliability and the added complexity could never be justified by the small energy saving involved. Only where domestic food is to be stored in seperate storage cellar.

## Domestic Swimming Pools

The applications to which the heat pump might be put in swimming pools, and for that matter in other sports complexes, are many and varied. It may be used in most swimming pool installations to recover heat from humid exhaust air, for heating of indoor swimming pool. It may be used in conjuction with ground water sources of one from another, to directly heat indoor or outdoor swimming pools. It can be also be combined with heat storage in such applications.

For indoor swimming pools ,the provision of hot water for additional services, over and above those for pool heating has been demostrated.

Outdoor swimming pools may have their water heated by heat pumps using outdoor air as the heat source, but as in most countries the need for pool heating coincides with high levels of sunshine.

# APPLICATION IN COMMERCE

## Shops And Clubs

Smaller commercial promises, such as shop clubs and restourants, share a number of relevant characteristics. In many countries they require both cooling and heating the need at particular time being dependt on bath whether and occupancy level. All of these characteristics favour the use of heat pumps for heating, cooling and ventilation. They are more economical to install and to control than separate heating and cooling systems and in addition have lower running costs. They may be airenged to provide large quantities of fresh air ventilation times of high occupancy.

## Central And Decentralised System

Centralised heat pump systems can combine heating, cooling, heat recovery and water heating. Heat produced with in the building can be collected and redistributed and ventilation exhaust can be recovered.

The decentralised systems may also be used to advantage in buildings which might require cooling during daytime but heating at night. If during daytime the water circuit is raised to its maximum permissible temperature while still effecting cooling of the order -of 32 0C- the heat in this circuit, provided that it is not rejected by the cooling tower to the atmosphere, may serve as a heat source during at least part of the heating cycle, before any form of supplementary heats part of the heating cycle, before any form of supplementary heats need to be added.